Telecommunications Carrier

NEBS Compliance Checklist

SIT.NEBS.TE.NPI.2002.010

November 4, 2003

Change Control Record:

| Version | Date | Action* | Reason for Revision |
| --- | --- | --- | --- |
| 1 | October1, 2002 | New | New Document prepared by the Verizon NEBS Compliance & Quality Assurance organization to simplify and improve understanding of carrier NEBS requirements. This document supercedes RNSA-NEB-95-0003 Revision 8 or higher. |
| 2 | January 24, 2003 | Change | Revised document to reference GR-63-CORE Issue 02, April 2002. Added reference to www.verizonnebs.com and Tech Updates. |
| 3 | October 8, 2003 | Change | Revised document to change Verizon organization name, to clarify manufacturer documentation, frame construction and altitude testing requirements. |
| 4 | November 4, 2003 | Change | Removed revision marks, added GR-909-CORE and GR-57-CORE to Table 2. |
| * New, Add, Delete, Change |  |  |  |

Prepared By:

| Name, Title, Organization | Date |
| --- | --- |
| James Giacchi, DMTS – Verizon NEBS Compliance & Quality Assurance |  |

Approved By:

| Name, Title, Organization | Date |
| --- | --- |
| Ludwig C. Graff, Director – Verizon NEBS Compliance & Quality Assurance |  |

TELECOMMUNICATIONS CARRIER

NEBS REQUIREMENTS

1.	WHY THE TELECOMMUNICATIONS CARRIER NEBS COMPLIANCE CHECKLIST?	3

2.	NEBS INFORMATION	3

2.1.	OVERVIEW	3

2.2.	NEBS REQUIREMENTS	3

2.3.	DEFINITION OF REQUIREMENT AND OBJECTIVE	4

2.4.	CARRIER NEBS REQUIREMENTS COMPARED TO COLLOCATION NEBS REQUIREMENTS	4

2.5.	NEBS REQUIREMENTS COMPARED TO OTHER REQUIREMENTS	5

2.6.	COPYRIGHT, OWNERSHIP AND PERMISSIONS	5

2.7.	SUBMISSION OF CARRIER CHECKLIST APPENDIX B AND OTHER DATA	5

2.8.	TESTING COMPARED TO DESIGN INTENT	7

2.9.	OBTAINING NEBS GENERIC REQUIREMENTS DOCUMENTS	7

2.10.	EQUIPMENT TESTING	8

2.11.	MAINTAINING NEBS COMPLIANCE	11

3.	CARRIER AND COLLOCATED EQUIPMENT BASIC NEBS REQUIREMENTS	11

3.1.	APPLICABILITY	11

3.2.	CARRIER CLARIFICATIONS TO NEBS REQUIREMENTS	12

3.3.	COMPLIANCE REQUIREMENT	20

4.	CARRIER OWNED EQUIPMENT ADDITIONAL NEBS REQUIREMENTS	20

5.	WHERE TO REQUEST NEBS COMPLIANCE INFORMATION OR SEND NEBS CHECKLISTS, REPORTS AND DATA	23

APPENDIX A – Test Report Certification

APPENDIX B – NEBS Compliance Checklist

# WHY THE TELECOMMUNICATIONS CARRIER NEBS COMPLIANCE CHECKLIST?

## All equipment deployed in a carrier’s Central Office (CO) equipment space or data rooms must be safe and pose no risk or safety hazard to any personnel, other nearby equipment or the physical structure.  The carrier also requires that equipment used for service to its customers must be able to deliver dependable and reliable performance during the conditions encountered under normal and abnormal circumstances.

## The Network Equipment Building Systems (NEBS) generic requirements are one of the mechanisms that are used to provide this safety and reliability.  Some NEBS testing and design requirements help make the equipment operate properly and safely; other NEBS requirements enable lower initial and ongoing operating costs for the carrier.

## NEBS is also recognized by financial risk assessors, municipalities and regulatory agencies as a major factor in a carrier’s ability to provide reliable, safe and cost efficient service to its customers.  Loss management and municipal agencies recognize the value of NEBS in reducing hazardous conditions and liability risks.  A lack of NEBS compliance could raise the cost of deployment of a given product a prohibitive amount.

## The NEBS requirements allow a carrier to use a single, uniform set of rules to evaluate fairly and impartially all equipment to be placed in the central office environment – whether the equipment is owned by the carrier or placed in leased space by other companies.

## The Telecommunications Carrier NEBS Compliance Checklist is a compendium of what Verizon believes are best industry practices, and do not necessarily reflect other carriers’ criteria or policies.  It is intended to help telecommunications carriers, equipment suppliers and independent testing laboratories by providing a first step toward a complete, common, standardized reference for NEBS compliance testing.

## Unless specified otherwise, Verizon Communications requires conformance to all portions of this document.  Statements that use the term ‘some carriers’ or optional are not Verizon requirements and are optional for the manufacturer when testing is being performed for Verizon.  The manufacturer should check with non-Verizon carriers for their requirements and the applicability of this checklist.

# NEBS INFORMATION

## OVERVIEW

### This document is intended to assist carrier and CLEC suppliers in understanding and meeting NEBS requirements and to explain or clarify carrier concerns and expectations.  The NEBS requirements are described in GR-63-CORE, GR-1089-CORE, GR-78-CORE and other documents referenced in Section 2.9.

### This document may be revised without notice.  The current version of this document is always available on the Verizon NEBS web page www.verizonnebs.com.  In addition, clarifications and interpretations of this document will be posted in the Technical Updates section of www.verizonnebs.com.  Always retrieve a new copy of the Telecommunication Carrier Checklist and check the Web Page Technical Updates section before using this document.

## NEBS REQUIREMENTS

### Carriers DO NOT waive NEBS requirements.  All applicable requirements must be tested.  No test facility, supplier, or consultant may decide what requirements or objectives may be altered or omitted unless the carrier’s NEBS compliance organization is consulted in advance.

#### The carrier reserves the right to determine which requirements or objectives may or may not be required.  See Section 2.7.5.

#### The final determination of all issues regarding applicability, pass/fail requirements or intent shall be decided by the carrier’s NEBS compliance organization.

### The carrier reserves the right to determine which requirements or objectives may or may not be required.  See Section 2.7.5.  Certain NEBS requirements may not be applicable for all equipment/systems under certain conditions.

#### A sufficiently detailed explanation shall be provided for all such requirements.

#### The carrier’s NEBS compliance organization will determine the suitability of such explanations.

### All equipment that is being evaluated for NEBS compliance for use by the carrier or a collocator must meet the current NEBS requirements that are in effect at the time the equipment is being evaluated for deployment, not the time the equipment was tested.

## DEFINITION OF REQUIREMENT AND OBJECTIVE

### GR-63, GR-1089 and others list the required tests under the following designations:

#### Mandatory Requirement (R): Testing is required; passing is required.

#### Objective (O) desired requirement: Testing is required; passing is the objective unless otherwise noted in this document.

#### Conditional Requirement (CR): Same as ‘Mandatory Requirement’, however, certain conditions as determined by the carrier may apply.

#### Conditional Objective (CO): Same as ‘Objective’, however, certain conditions as determined by the carrier may apply,

## CARRIER NEBS REQUIREMENTS COMPARED TO COLLOCATION NEBS REQUIREMENTS

### The following chart shows the relationship of the various elements of the NEBS requirements to reliability and risk.  It should be noted that most of the NEBS requirements are intended to ensure that equipment being tested provides reliable, safe service during normal and abnormal or stress operating conditions.

### Products intended for use in the carrier’s network applications are required to conform to all applicable reliability and risk or safety hazard related NEBS elements.

### Products intended for use in collocator’s network applications are required to conform only to the risk or safety hazard related NEBS elements.  See the left column in the table below and Section 3 for additional information.

### Summary of NEBS Risk, Safety and Reliability Elements.  See Sections 3 and 4 for details.

| NEBS Element Intended to Protect: |  |
| --- | --- |
| Minimal requirements for all equipment placed in Central Office environment: (Risk or Safety Hazard Related - “CLEC Level 1” Requirements) | These requirements are in addition to the minimal requirements for equipment providing carrier services |
| GR-63 2.0 Spatial Requirements | GR-63 |
|  | 4.1 Thermal Operating Conditions |
| 4.1.4 Heat Release & Surface Temperature |  |
| 4.2.2 Self-Extinguish/Fire Spread & Smoke Measurements |  |
| 4.2.3 Fire Resistance |  |
| 4.2.4 Smoke Corrosivity |  |
|  | 4.3 Handling/Transportation |
| 4.4.1 Earthquake |  |
| 4.4.2 Framework and Anchor Criteria |  |
|  | 4.4.3 Vibration |
|  | 4.4.4 Transportation Vibration |
|  | 4.5 Airborne Contamination |
| 4.6 Acoustic Noise |  |
|  | 4.7 Illumination |
| GR-1089 | GR-1089 |
|  | 2.0 ESD Immunity |
| 3.2 EMI Emission (10KHz through 10GHz; Open Doors) |  |
|  | 3.3 EMI Immunity |
| 4.0 Lightning and AC Power Fault (2nd Level) | 4.0 Lightning and Power Fault (1st Level) |
|  | - Steady-State Power Induction 6.0 DC Potential Difference |
| 7.0 Electrical Safety |  |
|  | 8.0 Corrosion Requirements |
| 9.0 Bonding and Grounding |  |
| GR-78 | GR-78 |
| Not Required | All Sections |

## Table 1.

## NEBS REQUIREMENTS COMPARED TO OTHER REQUIREMENTS

### NEBS requirements are intended to ensure that equipment and systems provide reliable service when less than ideal conditions are encountered without disrupting other services provided by nearby carriers or 3rd party owned equipment and without posing undue safety risks and hazards.  Other standards commonly used are either unidirectional or limited in scope.

### Many NEBS tests verify the ability of the equipment under test to function reliably during the testing as well as after the tests.  Other requirements and standards are either vague on this issue or permit functional testing to be done after the tests are completed.

### Manufacturing equipment that is NEBS compliant is the vendor’s responsibility and makes the vendor responsible for the replacement or renovation of equipment that is not NEBS compliant.  The cost of such changes is borne by the vendor and may not be limited to the cost of physical mitigation such as fire resistant partitions, electromagnetic shielding, etc.

## COPYRIGHT, OWNERSHIP AND PERMISSIONS

### Verizon Services Corporation holds all copyrights regarding this document.  Verizon Services Corporation hereby grants permission to other companies to use this NEBS Requirements document and Appendix B for the purpose of providing a standardized method to submit certain data necessary for NEBS compliance analysis.  Verizon Services Corporation retains all ownership rights to this document and Appendix B as well as all previous versions and reserves the right to make future revisions from time to time.  Alterations made by any company for its own use shall be clearly indicated via the use of a distinct and unique typeface for all alterations.  This paragraph shall be included in all such copies or uses.

## SUBMISSION OF CARRIER CHECKLIST APPENDIX B AND OTHER DATA

### The carrier will use the NEBS Compliance Checklist Appendix B to initiate assessment of equipment to be deployed within carrier network equipment space.

### The carrier NEBS Compliance Checklist Appendix B must be completed and returned promptly to ensure that all equipment placed in the carrier central office equipment space meets NEBS Requirements.

### The information required for CLEC (Competitive Local Exchange Carrier) applications is noted as “Required for CLEC” in Appendix B.

### Acceptance will be based on the degree of compliance of a supplier’s specific product to the NEBS family of requirements (GR-63-CORE, GR-1089-CORE, GR-78-CORE), originally published by Bellcore (Bell Communications Research, a.k.a. BCR), now Telcordia.  See Section 2.9.

### Additional carrier requirements and clarifications are identified in Sections 3.2 and 4.2, and highlighted in bold italic in Appendix B, F1 through F17.

### The NEBS Compliance Checklist Appendix B, with all blanks filled in, and associated data and reports must be submitted by the supplier to the carrier NEBS compliance organization.

#### The submitted form should include an action plan and time schedule for any non-compliant results.

#### The Checklist Appendix B should be completed using clear and concise wording and terminology.

#### All blank spaces in the Appendix B shall be properly completed or filled in – no abbreviations shall be used.  Partial, incomplete or missing information on a submitted Appendix B will delay the analysis.

#### Pre-printed statements or measurement units may not be altered.  Additional information shall be submitted via additional pages as needed.

#### “Design Intent, Conforms by Design, Conforms by Analysis” and other similar phrases are generally considered to be ambiguous claims and are inadequate explanations.

#### Ambiguous abbreviations, e.g., N/A, should be avoided when completing Appendix B.  If Not Applicable is used a detailed explanation is required.

#### Appendix B may be submitted via e-mail to the appropriate address noted in Section 5.

#### Appendix B should be submitted with current data, as it is known at the time of submission. A supplemental or updated Appendix B may be submitted as additional data becomes available.  It is the responsibility of the supplier and the appropriate carrier contact person to ensure that supplemental Appendix B submissions and test reports are provided in a timely manner to the carrier NEBS compliance organization.  A supplemental or updated Appendix B may be provided as work progresses and shall clearly indicate new or changed information. New or additional data should be clearly, e.g., bold, italic, highlighted, color, etc., noted on the subsequent submittals.

#### All test data and lab reports submitted to the carrier must be preceded or accompanied by a current version of the Carrier NEBS Compliance Checklist Appendix B.

#### Any Appendix B received that does not include the specific project or application for the product and a carrier contact person for the product will be considered to be unsolicited material and may not be reviewed.  Please note that members of the carrier NEBS Compliance team (Section5) are not the carrier contact interested in using the product.

#### The NEBS Compliance Checklist Appendix B, Item A Project Application/Description shall indicate the intended application/location for the equipment installed in the carrier’s facilities.  For example, the Item A shall indicate if the HOST/REMOTE, COT/RT, etc. equipment will be installed in carrier CO space.

#### Only the Appendix B, not this entire document, fully and properly completed should be submitted. Any blank space is generally considered to be missing data.

### Test Report Certification.  A completed Test Report Certification, Appendix A, must be attached to each test report.  The carrier will not accept test reports without accurate and complete certifications.  Please direct any questions to the carrier’s NEBS compliance contact.  Submit reports and certifications to the carrier’s NEBS compliance organization per Section 5.

### Independent Laboratory test reports and videos shall be provided upon completion of testing.  All reports shall be provided as both color hard copies and Adobe Portable Document Format (pdf) files on CD-ROM.

### The carrier’s NEBS compliance organization will review the Appendix B and all supporting data to determine product acceptability based solely on the carrier’s NEBS compliance organization’s interpretation of the intent of the requirements listed in GR-63-CORE, GR-1089-CORE and GR-78-CORE.

### The carrier’s NEBS compliance organization may work directly with the supplier to resolve any compliance issues identified in the data provided.  However, the carrier contact person will be responsible to ensure that the supplier fulfills the requirement to provide the data.

## TESTING COMPARED TO DESIGN INTENT

### Testing is required to prove compliance with NEBS Requirements.  Compliance statements are inadequate without test results or other substantiating information that is acceptable to the carrier’s NEBS compliance organization.

### Under circumstances as agreed upon by the carrier’s NEBS compliance organization, certain field experience data may be acceptable.

### Upon receipt of the required test data, the suitability of the equipment will be determined and deployment strategies evolved.

### If tests are in progress or planned, a Checklist must be provided and show expected completion dates.

## OBTAINING NEBS GENERIC REQUIREMENTS DOCUMENTS

### The equipment supplier is expected to obtain the necessary copies of the documents listed below from Telcordia, formerly Bellcore:

| - GR-63-CORE Issue 02, April 2002 | - Network Equipment Building System – Generic Equipment Requirements - -Describes Physical Requirements (Formerly TR-NWT-000063) |
| --- | --- |
| - GR-63-CORE Issue 02, April 2002 Errata | - Corrections to the GR-63-CORE Issue 2 developed after meeting with users of the document. (Available on www.verizonnebs.com in the tech tips section). |
| - GR-1089-CORE Issue 2, - December 1997 | - Electromagnetic Compatibility and Electrical Safety Generic Criteria for Network Telecommunication Equipment - -Describes EMC, ESD, and Electrical Safety Requirements (Formerly TR-NWT-001089) |
| - GR-78-CORE Issue 1, September 1997 | Generic Physical Design Requirements for Telecommunications Products and Equipment -Describes General Manufacturing Techniques for Equipment Reliability (e.g., connector types; contact mating surfaces; mixed metal avoidance; tin whisker avoidance; circuit trace sizing and spacing; component materials and composition). (Formerly TR-NWT-000078) |
| - TR-NWT-000295 Issue 2, July 1992 | ISOLATED GROUND PLANES: Definition and Application to Telephone Central Offices -Describes grounding methods for metallic frames and electrical power supplies associated with Central Office electronic Stored Program Control Switching Systems that are installed as an Isolated Ground Plane. |
| - GR—1274-CORE Issue1, May 1994 | Generic Requirements for Reliability Qualification Testing of Printed Wiring Assemblies Exposed to Hygroscopic Dust – Describes component testing under dust conditions for system performance. |
| - GR—3028-CORE Issue1, December 2001 | Thermal Management In Telecommunications Central Offices: – Provides thermal management information, guidelines, targets, Objectives, and Requirements for equipment manufacturers and service providers for ensuring network integrity. |
| - GR-909-CORE, March 2000 | Generic Requirements and Objectives for Fiber in the Loop Systems |
| - GR-57-CORE, October 2001 | Functional Criteria for Digital Loop Carrier Systems |
| ### Contact Telcordia Customer Relations at 8 Corporate Place, Room 3A-184, Piscataway, NJ 08854-4156, 800-521-2673, 732-699-5800 for further information. |  |

Table 2.

### The following GR/TR documents are sometimes mistaken as alternatives to the NEBS Generic Requirements.  These GR/TR documents pertain to various types of outdoor structures or enclosures, and do not necessarily pertain to the testing of equipment installed therein.  Requirements set forth will allow such structures to provide a suitable environment for any active or passive equipment installed therein.

| - GR-26-CORE Issue 1, - December 1994 | - Generic Requirements for Controlled Environmental Vaults (CEVs) |
| --- | --- |
| - GR-487-CORE Issue 1, - June 1996 | - Generic Requirements for Electronic Equipment Cabinets |
| - GR-950-CORE Issue 1, - December 1994 | - Generic Requirements for Optical Network Unit (ONU) Enclosures |
| - GR-2832-CORE Issue 1, - December 1994 | - Generic Requirements for walk-in Cabinets |
| - TR-NWT-000043 Issue 2, - November 1992 | - Generic Requirements for Telecommunications Huts |
| - TR-NWT-000357 Issue 2, - October 1993 | - Generic requirements for Assuring Reliability of Components Used in Telecommunications Equipment |

## Table 3.

## EQUIPMENT TESTING

### TEST FACILITY AND CHARGES

#### The supplier shall be responsible for all costs/charges associated with compliance testing.

#### Telecommunication carriers have various requirements for lab testing.  Please contact the appropriate carrier for detailed information before beginning equipment testing to make certain your test plans meet requirements.  Test results that do not meet carrier requirements will not be accepted.

### TEST DOCUMENTATION

#### The NEBS Compliance Checklist Appendix B is a vehicle for reporting testing and product information but is not accepted without supporting test data.

#### The supplier must furnish sufficient documentation to substantiate to the carrier’s NEBS compliance organization that NEBS testing was done per the stipulated procedures, methods, and ranges in the NEBS family of documents, referenced in Sections 2.9.1, 3.2 and 4.2.

#### Suppliers shall ensure that the selected test facility is familiar with the documentation criteria noted throughout this document.

#### The carrier NEBS compliance organization will not return test reports and videos.

#### Lab reports, written documentation, fire spread and earthquake videos, etc. should specifically reference the appropriate GR-63, GR-1089, GR-78 section(s) covered by the report.

#### Lab reports should specifically report test results by referencing the appropriate GR Requirement (R) or Objective (O) numbers.  Paragraph numbers are optional.  See Sections 2.2.

#### Lab reports and documentation shall report test conditions and observed characteristics of the equipment during testing.  Explanations of conditions and reactions shall be included as appropriate, including descriptions of failures and errors and the impact on the functional performance of the equipment.  Reports shall refrain from injecting opinions into the body of the observations.  Opinions may be grouped together in a specifically labeled report section.

#### Tested equipment configurations and a list of all equipment modules used in the test configurations shall be included.  The list shall include the module name/designation, model number, and part/ordering number. Any equipment modules not used in a tested configuration shall be listed as not tested.

#### Test data, reports, and videos shall be submitted complete and intact, that is, as originally printed and bound by the test facility.  Reports that are missing information or are re-packaged by a supplier may not be acceptable.

#### All test reports, data, and documentation shall be submitted via both paper hard copy and electronic soft copy media formatted via Adobe Acrobat 4.0, MS WORD 97, MS EXCEL 97 or an earlier compatible format.

#### Minor updates to reports, up to 10 pages, may be provided via e-mail, fax or electronic media formatted via Adobe Acrobat 4.0, MS WORD 97, MS EXCEL 97 or an earlier compatible format.

#### Suppliers and lab facilities are reminded that a Root Cause Analysis (RCA) is required for all tests that have failed, including those of GR-63-CORE, GR-1089-CORE and the tests specified in this document, even if subsequent re-testing is successful. (GR-63; R4-1, R4-2)

##### RCAs must include an explanation of what failed, why it failed (i.e., what caused the cause of the failure) and corrective action description.

##### Manufacturing cut-in dates, serial numbers, product ID changes, ordering requirements, availability, etc. for equipment incorporating the corrective action should be included in RCAs.

### TEST METHODS or PROTOCOLS

#### The NEBS Generic Requirements documents describe the procedures, methods and range criteria to be used to do the NEBS tests and the acceptable test result limits.  Suppliers and test labs are cautioned not to omit or modify portions of the test(s) without the carrier’s NEBS compliance organization’s prior agreement.

#### Compliance requires that the tests be performed as described in GR-63 and GR-1089 or other specifications and that the results meet the described limits.

#### Many of the various elements have multiple subsections and criteria.  If any of these subsections do not fully conform to the requirements, the entire section does not conform.  The supplier should report data by subsection if necessary.

#### Suppliers and test labs are cautioned not to abort a test in progress simply because a segment or requirement failed to pass.  The errors, failure mode, symptoms and performance should be documented in the report.  The failure mode and data are important in analyzing the ability of the equipment to function under the potential marginal conditions represented by the test.

#### Suppliers’ or manufacturers’ internal corporate standards and requirements are generally considered to be insufficient as a gating pass/fail requirement.  Use of these standards requires prior agreement with the carrier’s NEBS compliance organization and the standards must fully and specifically reference the NEBS family of documents.

#### Other references, protocols or test standards, e.g., UL, ETSI, EN, CISPR, FCC, IEC, CSA, should not be cited in reports as an additional reference, unless specifically authorized in the GR-1089 test description, since they are generally insufficient to establish NEBS compliance.

### SUPPLIER ACTION PLANS

#### For elements that “CONFORM,” provide a copy of the laboratory test data.

#### For elements that “FAIL to CONFORM,” provide a copy of the laboratory test data, an action plan and an explanation indicating when and how Compliance will be attained.

#### For elements that “PARTIALLY CONFORM,” provide a copy of the laboratory test data, an action plan and an explanation indicating when and how compliance will be attained.

#### Suppliers or manufactures shall provide detailed explanations of the reason any elements were not tested.  In general, all elements must be tested; however, there may be specific circumstances where testing may not be required.

#### NOTE:  The requirement is for testing to the NEBS criteria as described in GR-63-CORE and GR-1089-CORE.  However, if such tests are not yet completed, the supplier should in the interim provide available test data for other test protocols that may have been done. See Section 2.10.3 regarding other test protocols and associated limitations or concerns.

### EQUIPMENT CONFIGURATION

#### Suppliers shall ensure that the equipment to be tested is arranged so that all equipment slots or positions, e.g., circuit pack slots, are fully equipped to a worst case configuration with regard to floor load, heat release, fire resistance, fuel load, etc. The configuration shall include all representative circuit packs likely to be used or encountered by the carrier, even if the slot normally contains a circuit pack that is not being evaluated as part of the current test sequence.

#### All equipment shall be tested with the maximum number of components, printed circuit boards (PCBs), circuit packs, etc. the system will accommodate.  Once the configuration intended for the carrier is reached, the supplier may add additional PCBs that could be used in the equipment for different applications.

#### All equipment shall be tested in mounting arrangements representative of anticipated installations in carrier equipment spaces.  Worst-case configuration is required.

#### Refer to GR-63, Section 5.2.1 “The fire tests are conducted on materials and component configurations that replicate actual equipment frame assemblies, but need not be capable of functioning electrically (with the exception of internal equipment fans which may be operated).”

#### Refer to GR-1089, Section 3.5.5, Item 3 “The EUT power and signal leads should be, as nearly as possible, of the same length, orientation, and termination as they are in their normal operational configuration.”

#### Equipment shall be functioning, except for the fire spread tests, using acceptable call processing, application or load generating software that simulates normal traffic or operational loads.  Diagnostic exercises are generally not sufficient.

#### Equipment may not be functionally tested at a unit or shelf level unless it can properly perform the intended deployed function and is representative of the installed configurations likely to be encountered. Specifically, multi-shelf systems (e.g., a control unit and the units controlled) shall be tested at the frame level.

#### All workstations, terminals, monitors, modems, alarm units, ringing and tone generators, etc. that may be required for the equipment being tested and are permanently installed, i.e., ‘left in place,’ shall be included in the equipment test configurations.

#### Suppliers are encouraged to verify test plans and configurations with the carrier’s NEBS compliance organization before tests are done, to ensure the test configurations will be acceptable to the carrier.  Test plans should list all tests, provide detailed card layouts and indicate test points.  If a test is not being performed, it should still be listed and an explanation provided of why the test is not being performed.

#### If a supplier has a shelf level product but anticipates that multiple units will be used in a specific application, then the appropriate number of units should be placed in a rack and tested together as a system.  The carrier may not accept individually tested shelf units when they are combined with other like or different shelves for a specific application.

#### All supplier provided racks, frames and cabinets must be of welded, steel construction and meet the specifications of GR-63 section 3.1 (R3-1).

### OEM EQUIPMENT

#### The equipment supplier is responsible for ensuring that all OEM (Original Equipment Manufacturer) devices and subassemblies also meet the NEBS requirements.

#### The use of an OEM component or subsystem as a part of the larger system/application does not relieve any NEBS criteria.

#### The supplier or integrator of the final system or application provided to the carrier is responsible for attaining and maintaining NEBS Compliance.

#### The supplier or integrator of the final system or application provided to the carrier may provide the OEM’s test data if authorized by the OEM.  However, if the OEM equipment is integrated in a rack configuration with other equipment, the entire configuration must be NEBS tested.

## MAINTAINING NEBS COMPLIANCE

### The supplier is responsible for ensuring that NEBS Compliance is maintained throughout the equipment’s deployed service life in the carrier.  Specifically, it is the supplier’s responsibility to ensure that replacement, repaired or redesigned parts continue to meet the NEBS requirements.  The NEBS checklist Appendix B shall be resubmitted after every NEBS effecting change as determined by an ITL.  Examples of possible NEBS effecting changes include microprocessor changes, printed circuit board changes, component modifications and substitutions, back-plane modifications, enclosure modifications, etc.

# CARRIER AND COLLOCATED EQUIPMENT BASIC NEBS REQUIREMENTS

## APPLICABILITY

### Section 3 requirements apply to all equipment, including stand-alone test equipment, to be deployed in carrier network equipment space.  Both the carrier and collocated equipment are analyzed based on risk/safety/hazard related NEBS elements.  Some tests may not be applicable depending on the exact equipment configuration and application.  Please contact the carrier’s NEBS Compliance contact with any questions about the applicability of specific tests.

### generic requirements for risk, safety and hazard applicable for equipment located in carrier central offices.

GR-63 references: Spatial: - Section 2 Heat Dissipation: - Heat Release & Aisle Facing Surface Temp - Section 4.1, Sub-Section 4.1.4 Fire Resistance: - Section 4.2; Sub-Sections 4.2.2, 4.2.3, 4.2.4 Earthquake: - Earthquake zone requirements - Section 4.4, Sub-Sections 4.4.1.1, 4.4.1.2, & 4.4.2 Acoustic Noise: - Section 4.6 GR-1089 references: Emission Criteria: - Section 3.2; Sub-Sections 3.2.1 through 3.2.5 (Note: up to 10 GHz, with open doors) Lightning & AC Section 4; Sub-Sections 4.2.1, 4.2.2, 4.5.3, 4.5.4, 4.5.8, 4.5.10 (R-14), 4.5.11, Power Fault: - 4.5.13, 4.5.14, 4.5.15, 4.5.16, 4.6, 4.6.1, 4.6.2, 4.6.3, 4.6.3.2, 4.6.4, 4.6.4.2, 4.6.5 Electrical Safety: - Section 7 Bonding & Grounding: - Section 9, Sub-Sections 9.1 through 9.9

### Table 4.

### Additional requirements for carrier owned equipment are detailed in Section 4.

### The following required checklist items are applicable to all equipment.

#### Information items, including a complete list of shelves, modules and plug-in cards.  Refer to Appendix B items A to D

#### Spatial Requirements.  Framework, frames, racks, cabinets, etc. and non-powered or passive devices shall be considered equipment that must be tested.  Refer to Appendix B item F.1.

#### Heat Release and Aisle Facing Surface Temperature requirement and objective tests are required; carriers must provide a safe and comfortable environment for nearby personnel and equipment.  Internal unit temperatures of 130 F are not unusual and high surface temperatures pose a burn or safety hazard for personnel working in the vicinity.  Ambient operation testing is not required for collocated equipment. Refer to Appendix B items D14 through D17 and G.2.

#### Fire Resistance. Refer to Appendix B item G.3.

#### Testing for NEBS Earthquake/Seismic requirements and objectives is required.  Dislodged or loose parts, broken welds, etc. can pose safety hazards for personnel in the vicinity.  Office Vibration testing is not required for collocated equipment.  Refer to Appendix B item G.5.

#### Acoustic Noise Requirement.  Refer to Appendix B, item G.7.

#### EMI Emission testing up to 10GHz with cabinet doors open, as would be required to do maintenance activities is required.  Excessive emissions could impair the proper operation of other equipment in the vicinity.  Refer to Appendix B, item G.10.

#### NOTE: The carrier will accept test results/reports based on CLEC criteria only for collocation applications provided the specific risk and safety hazard data is supplied as described in Section 2.4.

## CARRIER CLARIFICATIONS TO NEBS REQUIREMENTS

### The following requirements represent specific areas of concern that, in the carrier’s opinion, are not adequately addressed by the GR requirements.  The requirements listed in this section are either specific clarifications or are in addition to the testing requirements listed in GR-63 and GR-1089.  These clarifications and additions are intended to address common questions from suppliers and test labs.   Contact the specific carrier for clarification on optional items.

### Optional weight limits.  Some carriers may limit the maximum weight of a single cabinet (fully populated, 24” deep) to 1150 lbs and the maximum weight of a single open bay (fully populated, 12” deep) shall not exceed 750 lbs.  Verizon follows the GR-63 floor loading limits.

### Optional network equipment size limits.  Some carriers may limit equipment (when installed in its bay/cabinet) to no larger than 30” in width, 24” in depth, and 7’ in height (or the standard ETSI- equivalent that is slightly higher).  Please note, however, that even though the preference is for no more than 24” in depth, smaller (space-saving) footprints for equivalent functionality and power are always desirable.  Equipment dimensions should attempt to follow typical sizes within the industry (i.e., 30”x24”x7’, 26”x12”x7’, 26”x14”x7’) to permit equipment of similar depth to be installed in the same row.  It is important to note this requirement does not mandate a particular size.  Verizon follows the GR-63 footprint and CO layout requirements.

### Power Requirements – Appendix B, item B

#### Equipment shall be powered by a -48 volt (nominal) DC power source and should be able to operate when between -40 and -57.5 volts DC is applied at the unit input power lugs for each individual power source feed.

#### The use of AC powered equipment should be avoided in all equipment configurations.  AC powered equipment shall not be used in the Isolated Ground Plane.

#### AC convenience outlets.  Verizon does not allow AC convenience outlets other carriers may require them at specific intervals.  Check your carrier for their specifications.

### Spatial Requirements – Appendix B, item G.1

#### The carrier DOES NOT WANT any AC convenience outlets in any equipment installed in the Isolated Ground Plane used for switching systems.  GR-63, R2-20 and R2-21 do not require that outlets be provided; they merely stipulate how to provide outlets if ordered by the carrier.

#### The carrier requires that the supplier provide an accurate footprint, equipment width and depth.  ALL equipment has a footprint.  The footprint is the maximum width and depth of a frame/cabinet, real footprint, or the maximum width and depth of any equipment mounted in a frame/cabinet, virtual footprint.  See GR-63 O2-4 and O2-14.  Equipment mounted in racks/cabinets shall be contained within the overall footprint of the rack/cabinet.

### Thermal Requirements – Appendix B item G.2

#### Telcordia grouped certain risk and safety hazard data measurements into the thermal performance category.  The carrier considers GR-63 items R4-13, O4-14, and O4-15 to be risk and safety hazard requirements and requires testing for both carrier and CLEC equipment.

#### The carrier requires that the supplier provide aisle facing surface temperature data (GR-63, O4-15) and test results for GR-63, requirements R4-6 and R4-7.  Aisle facing surface temperature of equipment shall never exceed 38 degrees C (100 degrees F) at an ambient room temperature of 26 degrees C (79 degrees F).

#### Some carriers require testing to GR-3028 Objective 5-4 (Rate of Change Test) page 5-8, Verizon does not

#### The carrier requires submission of an electronic copy of the GR-3028 Equipment Specifications Form (Appendix F) for use in NEBS Analysis and Equipment Planning.

#### Carrier Equipment and room cooling class preferences.

##### Combinations of Vertical Overhead Air-Distribution (VOH) and Horizontal Overhead Air-Distribution (HOH) room classes will be most prevalent going forward.

##### The majority of equipment bays in carrier buildings are capable of supporting an average heat release of between 10 and 40 watts per square foot.

##### The carrier has a strong preference for equipment with conforming heat release for the VOH and HOH room classes.  There is a strong preference for equipment classes with the bottom front-to-top rear (EC-Class F1-R3) airflow protocol for equipment in the central office environment at both frame - and shelf - levels. Bottom front-to-top (EC-Class F1-T) and mid front-to-mid rear (EC-Class F2-R2) protocols are also acceptable. Protocols that exhaust air to the front, bottom, or side of the frame are strongly discouraged.

#### The carrier requires that the supplier provide accurate heat dissipation and heat release information as described in GR-63 Section 4.4.1, R4-13, O4-14, and Table 4-6.  Data shall clearly note if values are for a steady-state maximum configuration or if typical heat release varies with traffic load or specific configuration. (Some carriers limit heat release to 80Watts per square foot and prefer 50Watts per square foot check with the specific carrier for their limits.)

#### If heat dissipation/release varies with load, e.g., talk-battery for subscriber lines, data shall show values for typical CCS levels, 12 CCS, 18 CCS, 24 CCS, and 36 CCS.  If applicable, the effect of loop length shall also be included in the values provided.

#### Heat release calculations should include ½ the front and rear aisle width and the width of the frame or rack mounting rails.  They should use the actual measured power dissipated by the equipment, not the fuse value of the power source times the voltage.  Heat release for shelf level equipment must also be adjusted for the shelf height by multiplying the heat released per square foot number by 12 and dividing by the equipment height in inches.  The worksheet below may be used to perform the heat release calculation.  The aisle allowance assumes 30-inch front and 24-inch rear aisles.  If door swing requires a larger aisle, use the larger number.

#### Heat Release and Footprint Calculation Worksheet

|  | #### 19” Rack Mounted | #### 23” Rack Mounted | #### Vendor Provided Cabinet |
| --- | --- | --- | --- |
| #### a) Equipment Depth in inches (12” minimum, increased to the next 6” value i.e., for 14” depth use 18”) |  |  | #### (Use Actual depth, increased to the next 6” value) |
| #### b) Aisle allowance | #### 27” | #### 27” | #### 27” |
| #### c) Add a and b |  |  |  |
| #### d) Equipment Width in inches | #### 23” | #### 27” | #### (Use Actual width) |
| #### e) Foot Print in square feet (multiply c times d, divide by 144) |  |  |  |
| #### f) Equipment Heat release in watts. |  |  |  |
| #### g) Frame Level Heat Release in watts per square foot (f divided by e) |  |  |  |
| #### h) Equipment Height in inches |  |  |  |
| #### i) Shelf level heat release in watts per square foot per foot (12 times g divided by h) |  |  |  |

### Fire Resistance Requirements – Appendix B item G.3

#### The carrier requires that supportive data be provided to warrant the pass/fail status of each of the sub-criteria elements listed for R4-15 and R4-20 fire spread criteria.

#### Tests are expected to identify any fire resistance, self-extinguish ability, and fire-spread issues that MUST be corrected.  Smoke analysis should be provided to indicate the particulate content and corrosivity.

#### Generic Guidelines for Fire Spread Testing

##### The equipment assembly must be configured as it will be configured for installation in a Central Office for all NEBS tests.

##### A rack must be fully assembled with all components/shelves, cables, hardware, cable trays etc.  All cables shall be dressed up the side of the frame.

##### A non-working sample may be used.

##### The fans must be operational at the beginning of the fire test.  The fans should be powered through their normal control circuitry, if possible; otherwise they must be powered from an external power source.

##### EUT must be pre-conditioned to 20ºC to 27ºC and a RH 50% (GR-63 Section 5.2.1).

#### GR-63 Test Configurations

##### GR-63 covers typical switch configurations for line burner placement.  GR-63 does not address platform and many switch-based designs.  Multiple fire-spread tests will most likely be necessary.

#### GR63 - Test Set UP

##### Fire test setup critical elements.  GR-63 Test Configurations cover line burner placement (LBP) for typical switch configurations and do not address platform and some switch based designs.  Most equipment will probably require multiple fire-spread tests.

##### Equipment test plan.  The test plan should consider the fuel load of each card and compartmentalization within the equipment's shelves and racks.  All compartments must be tested unless the compartments are identically configured or contain little or no fuel.  Multiple tests may sometimes be required in the same compartment depending upon its size and fuel load.  Control panels and fuse bays must be tested and raceways may not be removed.  Testing should start from the lower-most section of the equipment and work vertically up the unit for each test.  Follow GR-63 for the flame profile for each test.

##### Line burner placement.  If the width of a removable card is close to the size of the line burner, less than 1” remove the card and attach a blank faceplate, without a card attached to the frame.  Drill a hole through the bottom of the faceplate to accommodate the line burner.

##### Follow the instructions in GR-63 Section 5.2.3 for Equipment Assembly Fire Spread Test.  If a removable card is greater than 1” wide, leave the removable card in its slot and drill a hole through the bottom of the faceplate to accommodate the line burner so that the burner exposes the flames to the components.  If the line burner cannot clear the board, drill the hole below the card.

##### If the equipment has fans and they blow out the flame, follow the profile in GR-63 for Equipment Assembly Fire Spread Test.  If the fans continue to blow out the line burner and the burner gas flow of step 8 of the section 5.2.3 test procedure reaches 9 liters/M, leave the fans off and continue the test.  Do NOT start the test and then turn on the fans.

##### Test point selection.  The following diagrams show typical test point selections, indicated by the X, for common configurations.

Figure 1 - Typical CO environment.

X – Indicates line burner insertion.

Figure 2 - Platform with dissimilar components and compartmentalized shelves.

X – Indicates line burner insertion.

Figure 3 - Platform with dissimilar shelves and video monitor.

X – Indicates line burner insertion.

Figure 4 - Platform with Dissimilar Shelves.

X – Indicates line burner insertion.

Figure 5 - Platform fire spread test of four eight-inch shelves.

X – Insert line burner and rotate 90 degrees over top of circuit board.

#### The carrier uses the following smoke and self-extinguishing (fire) objective observation criteria to help minimize smoke hazards and fire spread from fires in equipment located in Central Office equipment spaces.  Equipment assembly fire tests shall be done in accordance with GR-63-CORE, (Section 4.2.2 requirements, and Section 5.2 test procedures) or any supplemental test configuration criteria that may be specific to the carrier on a case-by-case basis for certain equipment tests.  ALL of the following specific criteria shall be included in all shelf and frame level equipment assembly tests:

- After the conclusion of the methane ignition line burn (5 1/2 minutes after the start of the test), the components in the equipment assembly should show evidence of beginning to self-extinguish.

- At 10 minutes into the test (4 1/2 minutes after the ignition burner is turned off), there should be a significant flame reduction (or extinguished) and a visible reduction in the smoke from the equipment assembly.

- At 15 minutes into the test (9 1/2 minutes after the ignition burner is turned off), flames shall be extinguished, and there shall be only minimal wisps of smoke from the equipment assembly as determined from carrier review.

- If the smoke density measurements show any increase after the ignition burner is turned off (5 1/2 minutes after the start of the test), the length of time shall be measured until the smoke is completely eliminated.

- If the heat release measurements show any increase after the ignition burner is turned off (5 1/2 minutes after the start of the test), the length of time shall be measured until the equipment reaches ambient temperature.

- If during the initial ignition period of the Fire Spread Test, it is not possible to sustain a flame in the ignition line burner due to airflow from the fans extinguishing the flame, the fans shall be turned off.

- Thermal imaging videos are troubleshooting tools and shall be provided in the test results.  If the line burner is inserted in the front or rear of the product, the thermal imaging camera should view the same side of the product.  If the burner is inserted in the side of the product, the thermal imaging camera should view the surface, front or rear, which is expected to receive the most line burner heat.  The video should include a split screen of the thermal image and the image of the side in which the line burner has been inserted.  A second view of the rear or opposite side shall be provided on the same videotape.  More than two views on a split screen are not acceptable.  A real time running clock should be provided on all views.

- For a Fire Risk Analysis, the equipment supplier shall provide, upon request by the carrier, a database detailing the flammability characteristics of all equipment, materials, components, and wire and cable per GR-63-CORE.  An estimate of the maximum possible fuel load of polymeric materials in the fully equipped frame or subassembly should be documented (e.g., structural materials, electronic and electrical components, and associated wire and cable provided or specified by the equipment supplier).  This estimate should identify, in tabular format, the constituent items.  The estimate shall account for at least 95% of the maximum possible fuel load.  The remaining 5% should be described qualitatively in terms of types of polymers present.  A typical database should follow the format in the sample below.  The Module/Part Number heading should identify constituent items such as shelves, circuit boards, back planes, etc.  Integrated circuits, resistors, capacitors, LEDs, wiring, etc. should each have their own row with their part number and component description provided; column 7 should be totaled by component rating and for the complete module at the end of the table.

Module/Part Number: XYZ123

| Item # | Part Number | Component Description | Qty | Component Rating: UL-94 V0, V1 | Oxygen Index If >28% | Total Polymeric weight in grams | Comments |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | WXY | LED | 1 | V0 |  | 0.016 |  |
| 1 | XYZ | Carbon Resistor | 1 | HB |  | 0.006 |  |
|  |  |  |  |  | >28% | 0.008 |  |
| Totals |  |  |  | V0 |  | 0.016 |  |
|  |  |  |  | HB |  | 0.006 |  |
|  |  |  |  |  | >28% | 0.008 |  |

### Table 5.

### Earthquake Requirements – Appendix B item G.5.  Compliance to NEBS Earthquake standards is required for all carrier Central Office equipment, ironworks, frames and frame extenders.  The carrier requires Central Office equipment to be tested to the minimal specification of the Earthquake Zone where the product will be installed.  See GR-63 section 4.4.1 and GR-63 Figure 4-2 for detailed testing information.  Earthquake videos should be provided with the test documentation.

### Acoustic Noise – Appendix B item 7.   The equipment shall not independently, or as a part within a larger system, generate sufficient sound power as to violate OSHA requirements.  Further, the sound power shall be low enough that a Hearing Conservation Program is not mandated.  The time-weighted average sound power, measured using the OSHA measurement techniques, must be below 85 dB (A) over an 8-hour worst-case exposure and no sound of over 115 dB (A) shall be permitted.  As a given piece of equipment is just one source of sound power in a multi-source environment, the maximum permissible sound power for a given bay is 75 dB (A).  For a shelf-level system the maximum permissible system sound power is 65 dB (A).

### EMI Emission Requirements – Appendix B item G.10

#### Verizon strongly discourages the use of ferrites (for the purpose of EMI compliance) installed outside the shelf unit enclosure on all CO installations.

#### Testing must be done through 10 GHz.

#### Frequency plots shall clearly show all emissions.   Background emission evaluation and analysis is only required in the event the test results exceed the emission requirements or objectives.

#### Lab test reports shall include the measured emissions at the highest frequency tested.

#### In order to simulate normal operation, all cabling shall be connected and run in a vertical position, and dressed as shown in the diagram below. Once placed as shown below, no cable movement or rearrangement in an attempt to maximize emissions should be made.  An original picture and description of the test setup shall be included.

### Equipment type dependent sections – Appendix B item G.12 through G.16.

#### GR-1089-CORE Appendix A Application Guidelines Definitions categorizes equipment into four groupings or “Types.”

#### The supplier shall first determine which “Type” applies to the equipment to be tested.

#### The supplier shall then use GR-1089 Table B to determine the GR-1089 requirements that apply.  Requirements that are not applicable shall be referenced in the Checklist Appendix B item G.12 through G.16 with the appropriate “Type.”

### Bonding and Grounding – Appendix B item G.17

#### To meet the Frame Grounding Conductor safety connection requirements, GR-1089, R9-7 proposes two acceptable methods.

- Separate conductor(s) between the unit’s chassis and the framework.

- Thread-forming mounting screws with paint piercing washers that establish metal-to-metal contact.  This is the carrier’s preferred method.

#### The correct use of separate conductors requires that the conductor be sized to handle any fault current up to the limit of the circuit protection device feeding power to the equipment bay.  Any conductor, that is #6 AWG or larger must be connected using a 2-hole crimp type connector per GR-1089, R9-17 and TR-295.

#### Thread forming screws are not necessarily self-tapping or sheet metal screws.  Thread-forming screws are tri-lobular and establish threads by the plastic displacement of metal, instead of cutting threads, without creating metal chips or curls that could drop into other equipment.

#### The carrier’s preferred grounding method, thread-forming screws, used in lieu of a separate Grounding Conductor, must be used at all mounting positions and shall have an external tooth paint piercing lock washer between the head of the screw and the equipment unit.  No lock washers shall be used between the equipment unit and the framework.  Thread-forming screws shall also be used to attach any adapter/mounting brackets to the equipment unit.

#### The supplier shall provide installation instructions, with equipment shipments and with ITL NEBS test reports, that explain the purpose of the specific material provided and the correct use and installation.

## COMPLIANCE REQUIREMENT

### Lack of substantiating data, as described in this document, will be considered non-compliance.  All equipment considered for deployment in carrier Central Office equipment space will be evaluated based on compliance to all NEBS requirements.  See Section 2.2.

### NEBS compliance must be demonstrated by testing to the requirements in GR-63-CORE, GR-1089-CORE and carrier requirements as noted in Sections 3 and 4 and Appendix B.  These documents describe the test methods and procedures and the expected test result limits.

### No supplier or test facility shall base compliance on the use of a cabinet or enclosure to contain EMI or fire spread.  That is, cabinets shall not be relied upon to act as a barrier.  The equipment must meet the requirements.  Under certain conditions, the carrier’s NEBS compliance organization may prescribe the use of such cabinetry only as a (limited) mitigation measure.

### The supplier is expected to maintain NEBS Compliance for the product, throughout the equipment service life in the carrier, as described in TR-NWT-000357 “Generic Requirements for Assuring the Reliability of Components Used in Telecommunications Equipment.”

# CARRIER OWNED EQUIPMENT ADDITIONAL NEBS REQUIREMENTS

## APPLICABILITY

### This section provides clarification for some of the requirements, in addition to those described in Section 3, that apply to all carrier-owned equipment, including stand-alone test equipment, to be deployed in carrier network equipment space.  All suppliers are advised that the carrier requires full compliance to the requirements documents listed in Section 2.9 for carrier-owned equipment.  Some tests may not be applicable depending on the exact equipment configuration and application.  Please contact the carrier NEBS compliance organization with any questions about the applicability of specific tests.

## CLARIFICATIONS TO CARRIER ADDITIONAL NEBS REQUIREMENTS

### GR-78-CORE Requirements – Appendix B item F.

#### General Requirements for all products.

##### All piece parts, components, wire, and cable shall, where practical, be marked to be traceable to their original manufacturer; this requirement does not apply to structural metalwork and machined hardware such as screws.  On a temporary basis, part markings that fail to withstand assembly processing may be remarked with the original component markings.  This does not apply to markings identifying program-related information for programmable devices such as Erasable Programmable read-only Memories (E-PROMs).

##### The electrical and mechanical integrity and the reliability of all components and assemblies shall be retained after exposure to all processes employed during manufacture and assembly (e.g., handling, fluxing, soldering, and cleaning). It is the responsibility of the equipment supplier to demonstrate that each assembly and generic component type meets this requirement. Proof of the electrical and mechanical integrity of both components and assemblies shall be made available to the carrier.

#### Material and Finish Requirements.

##### Unless otherwise specified in GR-78-CORE or supporting documents, materials and finishes shall meet approved industry standards such that product integrity is not compromised for:

##### a) Whisker Growth – Tin, Zinc or Cadmium.

##### b) Fretting and Corrosion.

##### c) Dissimilar metal finishes.

##### d) Migrating silicon encapsulants near open contacts.

e) Material migration e.g., Solder.

### Optional power requirements, check with your specific carrier for applicability.

#### Equipment shall be powered by a -48 volt (nominal) DC power source able to operate between -40 to -57.5 volts DC as measured at the unit input power lugs for each individual power source feed.

Equipment shall be able to accept dual, independent -48 VDC power feeds and shall continue to operate from a single power source without manual intervention or interruption of functionality, including all LEDs, alarms and indications.  Each independent power feeder shall have its own battery return conductor.

“OR” diodes to combine power feeders may be used to power a network element from two power sources provided all the following requirements are met:

- Appropriately sized over-current protection devices shall be present in each power path to the unit, within the network element.

- Diodes shall also be included in each power path return of the unit.

- The maximum steady state current to be handled by the diode shall be limited to 50% of the diode’s maximum steady state current rating.

- Current transients shall not exceed the maximum rated value for the diode.

- The maximum reverse voltage across the diode shall be limited to 70% of the diode’s peak inverse voltage rating.

- The average junction temperature of the diode, within its normal operating environment, shall be less than 60 C, with the maximum allowed junction temperature being less than 110 C.

#### Power units shall have a low input voltage shutdown feature. The low input voltage shutdown shall occur when the input voltage measured at the input terminals of the equipment is between -39.5 and -37.5 VDC for greater than 100ms.  The preferred low voltage shutdown is -39.0 VDC.

#### Each DC-to-DC converter shall have a high output voltage shutdown feature.  The high output voltage shutdown shall occur when the output voltage measured at the DC-to-DC converter output terminals increases beyond 110 percent of normal output.

#### Equipment must be able to automatically recover from the low input voltage shutdown. The restart shall occur when the voltage measured at the input terminals of the equipment frame is –47.0 +/- 0.5 VDC.  The equipment shall return to pre-shutdown operation without manual intervention and without causing any over-current protection devices to operate.

### Noise Immunity - The equipment shall operate without failure with the presence of expected levels of electrical noise at its power-input terminals. The maximum noise levels in Table 7 are typical values. Wideband noise is defined as the rms voltage in any 3 KHz frequency band from 10 KHz - 20 MHz.  This test shall be performed on a plug-in, assembly, system or frame.  See Figure 1 of ANSI T1.315-1994 for test condition details.

#### Table 7

### Noise Returned from the Telecommunications Load Equipment - The noise returned by the telecommunications load equipment shall not exceed 56 dBrnC at 600 ohms.  See Figure 2 of ANSI T1.315-1994 for test condition details.

### Optional carrier thermal requirements – Appendix B item G.2.  Check with the specific carrier for additional information.

#### Some carriers may require modification of the temperature gradient in some GR-63-CORE test.  Check with your specific carrier for details.

#### The equipment must be tested and perform as expected in accordance with all the requirements within the specified operating temperature and humidity limits when installed in the altitude range of 200 feet below sea level to 6,000 feet above sea level.  Alternative test methods as described in GR-63 section 5.1.3, such as temperature compensation to simulate thermal altitude effects are not acceptable.  Some carriers may have additional or different altitude requirements.  Check with your specific carrier for details.

### ESD Immunity Requirements – Appendix B item G.5

#### The carrier requires that Severity Level 4 testing be done, as described in GR-1089 R2-1, R2-2, R2-3, O2-4, with any doors and covers fully open.

#### Wrist strap ground jacks must be external to any doors or removable covers to permit the wrist strap ground lead to be connected before any doors or covers are opened.

#### The lab test report shall list all components included in the test unit/system and shall specifically list or identify any functional abnormalities encountered during the sequence of test discharges.  ESD testing must be done on a fully configured functioning unit.

#### The lab test report shall list all points tested and provide a picture of the test setup.

#### Test points used shall be representative of areas or points commonly expected to be exposed to manual handling during installation, setup, adjustment, circuit pack replacement, etc.

#### The carrier supports and encourages the use of wrist straps to minimize ESD.  The carrier does not support, endorse, or permit the use of floor mats as abatement for ESD.

### Airborne Contamination Requirements – Appendix B item G.6

#### The carrier considers GR-63 Reactive Gases and Hygroscopic Dust conformance vital to assuring continued reliable operation in high humidity environments.  For equipment that is to be used exclusively in “Environmentally Controlled Space,” testing and conformance to GR-63 R4-60, indoor limits, is required.

### EMI Immunity Requirements – Appendix B item G.11

#### The carrier requires that EMI testing be done with doors or covers, if equipped, open (R3-8, R3-10).  CR3-9 and CR3-11 shall be considered Objectives, all failures must be analyzed and risk assessments performed.

#### EMI Immunity testing shall be performed through 10 GHz.

#### Cabling must use the same setup as 3.2.10.5 above.

### GR-487 Requirements – Appendix B item G.18

#### The carrier requires that GR-487 testing be performed on all equipment and cabinets assemblies that are for outdoor installation.

#### GR-487 Section 3.25 provides requirements for the Operating Temperature/Relative Humidity requirement of the electronic equipment installed in outdoor cabinets.  Verizon does not require specific modifications or additional testing for outdoor cabinets.  Contact the specific carrier for additional information.

##### The carrier and vendor will decide whether the solar loading or non-solar loading version of the test will be performed.

##### For tests with solar loading, the solar load is defined per GR-487-CORE specification, Section 3.26. Auxiliary heaters must be used to simulate solar load and are turned on at the elevated temperature +46C cycle level only.

##### For tests without solar loading, the chamber ambient temperature range shall be varied using the extended temperature range of 40C to +65C.  Ramp up and ramp down rates of the GR-63-CORE Figure 5-4, profile shall remain the same and the ramp up and ramp down times shall be extended until the indicated temperature is reached.  A successful test requires that the equipment be operated in a typical configuration for two full, consecutive failure-free GR-63-CORE Figure 5-4, profile test cycles.

# WHERE TO REQUEST NEBS COMPLIANCE INFORMATION OR SEND NEBS CHECKLISTS, REPORTS AND DATA

- All requests for NEBS compliance information or checklists should be sent to the appropriate company contact listed below or as provided by the carrier.

- E-mailing a checklist will expedite analysis.

Chuck Graff - Verizon Laboratories,

Director NEBS Compliance & Quality Assurance

320 St. Paul Place, 4th Floor

Baltimore, MD 21202

Tel:  410-736-5904

Fax: 410-736-5144

E-mail Ludwig.C.Graff@Verizon.com

###### Test Report Certification

A completed copy of this certification must be attached to each test report.  The carrier will not accept test reports without accurate and complete certifications.  Please direct any questions to the carrier’s NEBS compliance contact.

| Report Number | Name of Test Lab | Address of Test Lab | Report Date |
| --- | --- | --- | --- |

| Test Description | Name of Test Lab | Address of Test Lab | Date of test |
| --- | --- | --- | --- |

Independent Test Laboratory Director:  I hereby certify that the NEBS testing described in the indicated report was performed according to the NEBS requirements listed in the Telecommunications Carrier NEBS Checklist and the applicable Telcordia NEBS Generic Requirements.  I also certify that the testing was performed at the laboratory locations, dates and times listed above.

| Signature, Title, Organization | Date |
| --- | --- |

Manufacturer’s Test Laboratory Director:  I hereby certify that the NEBS testing described in the indicated report has been performed according to the NEBS requirements listed in the Telecommunications Carrier NEBS Checklist and the applicable Telcordia NEBS Generic Requirements.  I also certify that the testing was performed at the laboratory locations, dates and times listed above.

| Signature, Title, Organization | Date |
| --- | --- |

###### NEBS Compliance Checklist

(All applicable information must be provided to avoid evaluation delays.

Please direct any questions of applicability to the carrier’s NEBS compliance contact.)

A.  GENERAL INFORMATION   (Required for CLEC & Carrier Applications.)

| 1Date: |  | (Initial) |  |  | 2Date: |  | (Revised, All changes shall be clearly highlighted or identified) |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 3Carrier Contact: |  |  |  |  |  |  |  | 4RFP #: |  |
| 5NEBS Contact: |  |  |  |  |  |  |  | 6NEBS #: |  |
| 7Supplier Name: |  |  |  |  |  |  |  |  |  |
| 8Supplier Technical Contact: |  |  |  |  |  |  |  | 9Phone #: |  |
| 10Supplier e-mail address: |  |  |  |  |  |  |  | 11FAX #: |  |
| 12Equipment type/name: |  |  |  |  |  |  |  |  |  |
| 13System/Model Number: |  |  |  |  |  |  |  |  |  |
| 14Detailed Configuration Information: |  |  |  |  |  |  |  |  |  |

If equipment has optional configurations, modules, plug-in cards or circuit packs, a complete listing of modules/units must be included – please clearly show unit names, model numbers and plug-in card relationships. Attach lists and sketches of tested hardware units showing specific module locations, to this checklist. Complete the table below (items 15, 16 and 17) as required. Duplicate or repeat the table or lines as necessary.

| 15Shelf description: |  |  |  |  |
| --- | --- | --- | --- | --- |
| Manufacturer: | Model Name/Number: |  |  | Part Number: |
| 16Plug-in card or module descriptions for above shelf (List only one of each type:) |  |  |  |  |
| Model/Name: |  |  | Part Number: |  |
| 17Remarks for above shelf or plug-ins: |  |  |  |  |

| 18Carrier use (Yes/No): |  |  | 19Collocator use (Name): |  |
| --- | --- | --- | --- | --- |
| 20Project/Application description: Specify Function, Customer Premises, Host/Remote, COT/RT, number of sites, specific States/Cities, Carrier wide, etc.: |  |  |  |  |

B.  POWER REQUIREMENTS   (Required for CLEC & Carrier Applications.  See Section 3.2.4.  All items must be answered – Do not change any measurement units)

| 1-48v DC (Carrier Preferred): |  | Yes |  | No |  |  | Amps |  |  |  |  |  | Watts |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2Alternate/Additional Requirements: |  |  |  |  |  |  | Amps |  |  |  |  |  | Watts |  |  |  |  |  |  |  |  |
| 3Peripheral Equipment Requirements: |  |  |  |  |  |  | Amps |  |  |  |  |  | Watts |  |  |  |  |  |  |  |  |
| 4Is AC power mandatory for any system component: |  |  |  |  |  |  |  |  |  |  |  | Yes |  |  |  |  |  |  | No |  |  |
| 5Is this power information representative of a specific, typical or maximum configuration? |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 6List equipment voltage classification(s) per GR-1089, Section 7.2: |  |  |  |  |  |  |  | Class: |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 7Comments/Describe: |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |

C.  GROUNDING REQUIREMENTS    (Required for CLEC & Carrier Applications.  See Section 3.2.12.  Refer to TR-NWT-000295; this is not the same as UL 1950.  All items must be answered)

| 1 Does this equipment conform to the Integrated Ground Plane requirements in GR-1089 Section 9? |  |  | Yes |  |  | No |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2Is this equipment compatible with the TR-NWT-000295 for Isolated Ground Plane? |  |  | Yes |  |  | No |  |  |
| 3Is internal logic ground isolated from chassis/framework ground? |  |  | Yes |  |  | No |  |  |
| 3Is signal ground, external interface, isolated from chassis/framework ground? |  |  | Yes |  |  | No |  |  |
| 4Is chassis/framework used as a current carrying conductor? |  |  | Yes |  |  | No |  |  |
| 5Comments/Describe: |  |  |  |  |  |  |  |  |

D.  PHYSICAL SIZE/MOUNTING REQUIREMENTS    (Required for CLEC & Carrier Applications.  All items must be answered – Do not change any measurement units)

| 1 Is equipment a circuit pack, shelf, frame, rack, cabinet or multiple frames? Explain if required. |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2 Does equipment mount on a relay rack or cabinet included as part of system? |  |  | Yes |  |  | No |  |  |
| 3 Does cabinet or equipment unit/mounting have doors or removable covers on front? |  |  | Yes |  |  | No |  |  |
| 4 Does cabinet or equipment unit/mounting have doors or removable covers on rear? |  |  | Yes |  |  | No |  |  |
| 5 Is access to rear of relay rack/cabinet required for maintenance? |  |  | Yes |  |  | No |  |  |
| 6 Is cabling terminated on the front of equipment? |  |  | Yes |  |  | No |  |  |
| 7 Is equipment forced air-cooled by its own fan unit? |  |  | Yes |  |  | No |  |  |
| 8 Are air filters required? (Carrier does not approve the use of ‘re-usable’ filters). |  |  | Yes |  |  | No |  |  |
| 9Is equipment installed exclusively indoors in a CO, CEV, HUT, or customers’ Premises? |  |  | Yes |  |  | No |  |  |
| 10 Is Equipment installed exclusively outdoors in a metal enclosure? |  |  | Yes |  |  | No |  |  |
| 11 Equipment dimensions measured in normal mounting configuration. |  | Height |  |  |  |  | Inches |  |
|  |  | Width |  |  |  |  | Inches |  |
|  |  | Depth |  |  |  |  | Inches |  |
| 12 Minimum aisle clearance required for fully open door ‘clear swing’ – front. |  |  |  |  |  |  | Inches |  |
| 13 Minimum aisle clearance required for fully open door ‘clear swing’ – rear. |  |  |  |  |  |  | Inches |  |
| 14 Equipment footprint. (See 3.2.6.8 Heat Release and Footprint Calculation Worksheet line e.) |  |  |  |  |  |  | ft2 |  |
| 15 Equipment total weight. |  |  |  |  |  |  | Lbs. |  |
| 16 Equipment floor loading (GR-63: O2-18, R2-19). (Divide line 15 by line 14). |  |  |  |  |  |  | Lbs/ft2 |  |
| 17 Equipment heat release. (See 3.2.6.8 Heat Release and Footprint Calculation Worksheet line f.) |  |  |  |  |  |  | Watts Watts |  |
| 18 Equipment heat release (GR-63: R4-13, O4-14). |  | Frame: |  |  |  |  | W/ft2 |  |
| (See 3.2.6.8 Heat Release and Footprint Calculation Worksheet line g for a frame or I for a shelf.) |  | Shelf: |  |  |  |  | W/ft2/ft |  |
| 10 Does heat release vary with traffic load? |  |  | Yes |  |  | No |  |  |
| 20 Is heat release calculated for a specified traffic level? |  |  | Yes |  |  | No |  |  |
| 21 If yes, specify the traffic level used in the calculated heat release. |  |  |  |  |  |  | CCS |  |
| 22 Maximum Aisle Facing Surface Temperature (GR-63: O4-15). |  |  |  |  |  |  | oF |  |
| 23 Comments: |  |  |  |  |  |  |  |  |

E.  ALARM AND PERFORMANCE MONITORING INTERFACE

| 1 Do all fuse alarms provide audible, visual, local, and remote reporting? |  |  |  |  |  | Yes |  |  | No |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2 Does equipment include a provision for connection to local/remote external alarms and/or performance monitoring systems? |  |  |  |  |  | Yes |  |  | No |  |  |
| 3 Can alarms be transmitted to remote locations? |  |  |  |  |  | Yes |  |  | No |  |  |
| 4 Can alarms be retired from remote locations? |  |  |  |  |  | Yes |  |  | No |  |  |
| 5 Can alarms be ‘obscured’ by other (e.g., lower level) alarms? |  |  |  |  |  | Yes |  |  | No |  |  |
| 6 Does equipment interface require proprietary Operational Support Systems? |  |  |  |  |  | Yes |  |  | No |  |  |
| 7 Identify/Describe proprietary Operational Support Systems: |  |  |  |  |  |  |  |  |  |  |  |
| 8 Specify supported performance-monitoring interfaces. TNM/NFM, NMA, TONICS, SNMP, TL1, CORBA, others? |  |  |  |  |  |  |  |  |  |  |  |
| 9 Additional Comments or Descriptions: |  |  |  |  |  |  |  |  |  |  |  |

F. GR-78 PHYSICAL DESIGN REQUIREMENTS   (Required for Carrier Applications, All items must be answered.  See Section 4.2.1.)

| GR-78 Section | # Element Requirement Description | Compliant |  |  |  |  | # Exceptions and Remarks |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 3 | # Materials and Finishes Requirements |  |  |  |  |  |  |
| 3.1 | General: R3-4, R3-7 | Yes |  | No |  |  |  |
| 3.2.2 | Fire Risk Analysis: R3-10, R3-11 (Component Rating UL94, V-0 or V1), R3-12 | Yes |  | No |  |  |  |
| 3.2.3&3.2.4 | Fluxes: R3-14 / Silver - CR3-15 | Yes |  | No |  |  |  |
| 3.2.5 | Silicones: R3-16 | Yes |  | No |  |  |  |
| 3.3 | Finishes: R3-17-R3-20 (min 2% lead)-R3-23 | Yes |  | No |  |  |  |
| 4 | # Separable Connector Requirements |  |  |  |  |  |  |
| 4.1.1 | Design: Similar Metals - R4-1 - R4-20 | Yes |  | No |  |  |  |
| 4.1.2 | Noble Metallization - R4-21, R4-24 - 31 | Yes |  | No |  |  |  |
| 4.1.3 | Base metallization - R4-32 through R4-34 | Yes |  | No |  |  |  |
| 4.1.4 | Lubrication (Contacts) - R4-35 through R4-40 | Yes |  | No |  |  |  |
| 4.3 | Component Sockets: R4-66 | Yes |  | No |  |  |  |
| 4.4 | Insulation Displacement Connect. (R4-69) | Yes |  | No |  |  |  |
| 4.5 | Zero Insertion Force Connectors, R4-72 | Yes |  | No |  |  |  |
| 4.6 | Coaxial Connectors - R4-75 | Yes |  | No |  |  |  |
| 4.7 | Optical Connectors – R4-76 & R4-77 | Yes |  | No |  |  |  |
| 6. | # Printed Wiring Board Requirements |  |  |  |  |  |  |
| 6.1 | General - R6-1 | Yes |  | No |  |  |  |
| 6.1.1 | Materials – Laminates (R6-2 &3), Solder Mask (R6-4 & 5), Repair Polymers (R6-7) | Yes |  | No |  |  |  |
| 6.1.2 | Design – Interlayer Connection (R6-16-17) Warpage (R6-19), Protect Coating (R6-21) Resistance to Airborne Contaminant (R6-22) | Yes |  | No |  |  |  |
| 6.1.3.2 | Conductor Widths & Spacing (R6-26 -32) | Yes |  | No |  |  |  |
| 6.1.3.3 | Conductor Adhesion – R6-33 | Yes |  | No |  |  |  |
| 6.1.3.6 | Solder ability – R6-49 | Yes |  | No |  |  |  |
| 6.1.3.7 | Solder Masks – R6-50 through R6- 64 | Yes |  | No |  |  |  |
| 6.1.3.9 | Insulation Resistance Testing – R6-78 - 84 | Yes |  | No |  |  |  |
| 6.1.3.10 | Solvent Extract Conductivity - R6-85 - 93 | Yes |  | No |  |  |  |
| 6.1.3.11 | Mechanical Damage – R6-95 through R6-108 | Yes |  | No |  |  |  |
| 6.1.3.14 | Repairs – R6-122 through R6-133 | Yes |  | No |  |  |  |
| 6.2 | Multi-layer PWBs- General Requirement |  |  |  |  |  |  |
| 6.2.1.1 | Dimensioning – R6-165 through R6-174 | Yes |  | No |  |  |  |
| 6.2.1.3 | Construction – R6-175 through R6-180 | Yes |  | No |  |  |  |
| 6.2.2.3 | Plated-Through Holes - R6-183 - 188 | Yes |  | No |  |  |  |
| 6.2.2.5 | Insulation Resistance Testing – R6-192 | Yes |  | No |  |  |  |
| 6.2.2.6 | Solvent Extract Conductivity (SEC) Testing - R6-193 -196 | Yes |  | No |  |  |  |
| 6.2.2.10 | Repairs – Finished Multi-layer PWBs – R6-208 - 209 | Yes |  | No |  |  |  |
| 6.3 | # PWBs for Surface Mounting |  |  |  |  |  |  |
| 6.3.1.1 | Materials – laminates – R6-214 | Yes |  | No |  |  |  |
| 6.3.1.2 | Materials – solder masks – R6-215 | Yes |  | No |  |  |  |
| 6.3.1.3 | Component mounting pads – R6-216 -218 | Yes |  | No |  |  |  |
| 6.3.1.4 | Design – solder masks – IP6-222 | Yes |  | No |  |  |  |
| 6.3.1.6 | PWBs for adhesive-and wave solder, Soldering – Component Mounting Pads | Yes |  | No |  |  |  |
| 6.3.1.7 | PWBs for re-flow surface mounting soldering: Conductor finish - R6-228 | Yes |  | No |  |  |  |
| 7. | PWB Assembly Requirements |  |  |  |  |  |  |
| 7.1.1 | Materials: Conformal Coating (R7-1 – 2) Fluxes: R7-4 | Yes |  | No |  |  |  |
| 7.1.2.2 | Components: R7-19, 20, 21, 22 (no piggy –back component mounting allowed) | Yes |  | No |  |  |  |
| 7.1.2.4 | Layout: thermal component placement consideration – R7-33 - 36 | Yes |  | No |  |  |  |
| 7.1.2.6 | Layout: component lead forms, R7-48 - 52 | Yes |  | No |  |  |  |
| 7.1.3 | # Manufacturing |  |  |  |  |  |  |
| 7.1.3.3/4 | Soldering/Soldering: R7-84 through R7-95 | Yes |  | No |  |  |  |
| 7.1.3.5 | Warpage: R7-96 | Yes |  | No |  |  |  |
| 7.1.3.6 | Solder masks: R7-97 through R7-99 | Yes |  | No |  |  |  |
| 7.1.3.7 | Conformal coatings: R7-100 | Yes |  | No |  |  |  |
| 7.1.3.13 | Repair of PWB assemblies: Component removal and replacement: R7-117 - 126 | Yes |  | No |  |  |  |
| 7.1.3.17 | Modification to PWB: Wire routing, R7-138 through R7-142 | Yes |  | No |  |  |  |
| 7.1.3.19 | Modification to PWB – Soldering of modification wires – R7-148 (Prototype board assemblies, with plans to re-spin, and containing not more than five wires, may be temporarily permissible for a period not exceeding 6 months.), R7-149 - 151 | Yes |  | No |  |  |  |
| 8. | Equipment Sub-Assembly and Assembly Requirements |  |  |  |  |  |  |
| 8.1.3 (a) | Design: Accumulation of dust on telecommunication products can provide the potential for electrical breakdown: R7-6 through R7-10 | Yes |  | No |  |  |  |
| 8.1.3 (b) | Design: Fan or blower cooled equipment shall be fitted with suitable filters – R8-3 through R8-8 | Yes |  | No |  |  |  |
| 8.1.3 (c) | Design: ESD protective measures during equipment assembly maintenance – R8-23 | Yes |  | No |  |  |  |
| 8.1.3 (d) | Design: Contact breakers and other service-affecting switches shall be so designed as to minimize the risk of accidental activation during routine maintenance and operation. R8-25 | Yes |  | No |  |  |  |
| 9. | # Electrostatic Discharge |  |  |  |  |  |  |
| 9.4.2 | # Circuit Pack ESD Considerations: |  |  |  |  |  |  |
| 9.4.2.2 | Susceptibility – R9-1, R9-2 | Yes |  | No |  |  |  |
| 9.4.2.3 | Performance Criteria – R9-3 | Yes |  | No |  |  |  |
| 9.4.2.4 | Specifications – R9-4 through R9-7 | Yes |  | No |  |  |  |
| 9.5.1 | ESD Caution Labels – R9-19 | Yes |  | No |  |  |  |
| 10. | Product identification & marking requirements: R10-1, R10-4 – 7 | Yes |  | No |  |  |  |
| 11. | Package requirements: R11-1 through R11-10 | Yes |  | No |  |  |  |
| 12. | Repair and modification of customer return units: R12-1 through R12-8 | Yes |  | No |  |  |  |
| 12.2 | Marking – R12-9 | Yes |  | No |  |  |  |
| 12.3 | Repairs- (PCB charring) R12-10 - R12-14 | Yes |  | No |  |  |  |
| 13 | Qualification test: Fluxes requirement R13-1 | Yes |  | No |  |  |  |
| Comments: |  |  |  |  |  |  |  |

G. NEBS TEST RESULTS

G.1.    Spatial Requirements  (Required for CLEC & Carrier Applications)

GR-63, Section 2:	Specifies requirements for physical size of equipment framework, floor loading, line-up, aisle spacing, operations systems, cabling and cable entrance, front/rear access.  See Section 3.2.5.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.2.    Thermal Requirements   (Required for CLEC & Carrier Applications)

GR-63, Section 4.1:  Specifies temperature, humidity, and altitude range throughout which the equipment must be able to remain operable, and function normally.  See Section 3.2.6.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient |  |  | Date Sent: |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.3.    Fire Resistance Requirements  (Required for CLEC & Carrier Applications)

GR63, Section 4.      Limits frequency of fires and extent of damage due to the materials used, overheating, short-circuit damage, rate of flame spread, secondary fires from dripping flaming/molten material and smoke corrosivity.  The tests measure fire resistance by observing self-extinguish ability and flame spread of a burning unit.  The equipment’s fire hazard is characterized by measuring the radiant heat flux and heat release. Fire resistance estimates are less desirable than actual tests.  See Section 3.2.7.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.4.    Handling and Transportation Requirements (Required for Carrier Applications)

GR63, Section 4.3:	Ensures that equipment can be shipped without damage and arrives in serviceable condition.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.5.    Earthquake and Office Vibration Requirements  (CLEC - Earthquake only & Carrier Applications - All)

GR-63, Section 4.4:	 Ensures that seismic or building vibrations from adjacent construction, highways, etc., do not cause operational or performance problems. Nearby heavy machinery, heavy construction, heavy industrial equipment, truck/train traffic, building HVAC systems, or standby generators can result in low frequency vibration.  It is important to know if such low frequency vibration will cause long-term troubles such as connectors becoming loose, or short-term problems like disk drive crashes. See Section 3.2.8.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |  |
|  | Earthquake Zone |  |  | (Specify the Earthquake Zone that was tested.) |  |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |  |

G.6.    Airborne Contamination (Required for Carrier Applications)

GR-63, Section 4.5: Describes air quality (particulate) conditions under which equipment is expected to operate properly.  Particulate contamination, specifically soluble salts, can combine with water vapor and result in increased corrosion levels.  Organic vapors and reactive gases can aggravate corrosive actions and can affect disk drive and magnetic tape reliability. Hygroscopic dust contamination, R4-59, creates the potential for resultant intermittent or erratic performance.  See Section 4.2.7.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |  |

G.7.    Acoustic Noise Requirements  (Required for CLEC & Carrier Applications)

GR-63, Section 4.6: Limits noise levels than can emanate from equipment.  This requirement is intended to ensure that OSHA limits are not exceeded.  See Section 3.2.9

|  | Test Facility Name: |  |  | Test Date: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |  |

G.8.    Illumination Requirements (Required for Carrier Applications)

GR-63, Section 4.7:  Establishes requirements for surface reflectance and color intended to minimize reflected glare. It is intended to determine the readability of the stenciling and markings on the equipment, under the ambient light level normally encountered in CO equipment space. Surface finishes and colors, marking colors, styles, size should be clear and of high contrast and low glare, O4-66, O4-67. This requirement does not refer to lighting fixtures supplied or ambient light levels generated by the equipment.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |  |

G.9.    ESD Immunity Requirements (Required for Carrier Applications)

GR-1089, Section 2.0:  Ensures that equipment operation is not susceptible to ESD when normally accepted precautions are used.  The requirement is to do the tests.  The objective is to pass the test.  Lab test reports MUST specifically describe equipment functionality during the test discharges.  ANY abnormal or unexpected behavior or system degradation MUST be described.  Emphasis will be placed on the degree of service degradation. See Section 4.2.2.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |  |

G.10.    EMI Emission Requirements  (Required for CLEC & Carrier Applications)

GR-1089, Section 3.2:  Ensures that equipment does not emit excessive radiated or conducted emissions that could interfere with the proper operation of other equipment. Lab test reports must clearly show the emissions from the equipment, plotted against the acceptable GR-1089 limits, with the ambient background measurements overlaid on the graph.  Graphs should be color coded for clarity.  See Section3.2.10.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |

| Are external ferrites required for EMI Emission compliance?(Yes/No) |  |
| --- | --- |

| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |
| --- | --- |

G.11.    EMI Immunity Requirements (Required Carrier Applications)

GR-1089, Section 3.3:	Ensures that the equipment functions properly and that operation is not susceptible to radiated or conducted emissions from other equipment.  Lab test reports MUST specifically describe equipment functionality during the test.  ANY abnormal or unexpected behavior or system degradation MUST be described.  Emphasis will be placed on the degree of service degradation.  See Section 4.2.8.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |

| Are external ferrites required for EMI Immunity compliance?(Yes/No) |  |
| --- | --- |

| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |
| --- | --- |

G.12.    Lightning and AC Power Fault Requirements  (Required for CLEC & Carrier Applications)

GR-1089, Section 4.0:	Prevents or safely limits trouble when equipment is exposed to abnormal or fault conditions resulting from lightning surges and AC power fault conditions that may occur at network terminations.  See Section 3.2.11

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  | Equipment is Type: |  |  | (Enter type 1, 2, 3 or 4 from GR-1089, Appendix B) |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.13.    Steady-State Power Induction Requirements (Required for Carrier Applications)

GR-1089, Section 5.0:	Establishes requirements for equipment tolerance of induced, longitudinal (common mode) noise that may be experienced in telephone outside plant facilities.  See Section 3.2.11.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  | Equipment is Type: |  |  | (Enter type 1, 2, 3 or 4 from GR-1089, Appendix B) |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.14.    DC Potential Difference Requirements (Required for Carrier Applications)

GR-1089, Section 6.0:	Establishes requirements to ensure that equipment can operate properly when presented with a normally expected potential difference.  See Section 3.2.11.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  | Equipment is Type: |  |  | (Enter type 1, 2, 3 or 4 from GR-1089, Appendix B) |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.15.    Electrical Safety Requirements  (Required for CLEC & Carrier Applications)

GR-1089, Section 7.0:	Ensures that people using or working on or near the equipment are not exposed to hazards.  See Section 3.2.11.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  | Equipment is Class: |  |  | (Enter Class from GR-1089) |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.16.    Corrosion Requirements (Required for Carrier Applications)

GR-1089, Section 8.0:	Ensures that a zero or negative potential with respect to ground is maintained to prevent corrosion in outside plant cables when water accidentally enters the cable core.  See Section 3.2.11.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  | Equipment is Type: |  |  | (Enter type 1, 2, 3 or 4 from GR-1089, Appendix A) |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.17.    Bonding and Grounding Requirements  (Required for CLEC & Carrier Applications)

GR-1089, Section 9.0:  Ensures that safe and proper operation of this and other equipment is maintained. If this equipment or any component with a physical or electrical connection to this equipment is to be placed within the switch Isolated Ground Plane, conformance to TR-NWT-000295 (Isolated Ground Plane, Single Point Ground System) is required or Carrier NEBS Compliance approved mitigation measures must be used.  All grounding and bonding conductors must be of sufficient size, as described in TR-NWT-000295 and must use 2-hole crimp lugs based on conductor size.  Reference should be made to GR-1089 R9-7 for acceptable safety Frame Ground connection.  See Section 3.2.11.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

G.18.    GR-487 Requirements for Electronic Equipment Cabinets (Required for Carrier application of outdoor cabinets)

GR-487:	Ensures that safe and proper operation of telecom equipment to be placed in an outdoor environment.  The product requires testing to appropriate GR-63 and GR-1089 as directed and augmented by the GR-487 requirements.

|  | Test Facility Name: |  |  | Test Date: |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Report Number: |  |  | Report Date: |  |  |  |
|  | Carrier Recipient: |  |  | Date Sent: |  |  |  |
|  |  | Test Results | (Mark one row with an X.) |  |  |  |  |
|  |  |  | CONFORMS |  |  |  |  |
|  |  |  | DOES NOT CONFORM |  |  |  |  |
|  |  |  | PARTIALLY CONFORMS |  |  |  |  |
|  |  |  | PRODUCT NOT TESTED |  |  |  |  |
| Action Plan/Date: (Provide schedules/planned dates, re-tests, equipment modification notices, explanations, etc.) |  |  |  |  |  |  |  |

Telephony power plants are generally referred to as -48vDC systems.  These plants generally operate (a.k.a. float) at -52v to -54v DC with an equalize mode in some reaching -57v DC.  All equipment is expected to operate normally in these ranges and should operate without faults on a reduced supply voltage as low as -42v DC.  Supply voltages between -48v DC and -42v DC may be encountered during abnormal periods when the battery plant may be in a discharging mode as a result of power failures.